## 2022 Ann Return 27 SOs
[11 empty] | Historical spill counts |  |  | 2022 spill counts and durations | [5 empty] | Environmental impact data, where available | [9 empty] | Associated bathing waters, if applicable | Current Investment plan, if applicable |  |  | Future Investment plan | Past Imps
Storm Overflow ID | Site ID | Storm Overflow ID | Storm Overflow name | Permit Reference | Storm Overflow Type | Waterbody ID | Receiving Waterbody Catchment Name | Receiving Water / Environment (common name) | Shellfish Water | Bathing Water | Initial monitoring commission date | 2020 spill count | 2021 spill count | 2022 spill count | Total duration (hours) all spills in 2022 | % of reporting period monitoring operational in 2022 | Primary reason for monitoring <90% | Action taken / planned if monitoring <90% | High Spill Frequency - operational review - primary reason | Latest Aesthetic impact survey date | Aesthetic impact assessment | Latest Invertebrate impact survey date | Invertebrate impact assessment | Latest WQ impact survey date | WQ impact assessment | Other impact data collected | Comments | Ecological status of waterbody (web link) | Is the storm overflow located in a waterbody where the Reason for Not Achieving Good (RNAG) Ecological Status has been linked to Storm Overflows? Yes/No | Bathing water profile (web link) | Project Nr | Construction complete | What are we doing? | Construction complete | SO Imp Tech Desc | Date | Scheme TechDesc | Last 12 months EO spills | Storm overflow categorisation 27 June 2021
13056C | 13056 | 13056C | CHARMOUTH HEADWORKS/SEA OUTFALL WRC - SO | 401625 | Inlet Storm Overflow at WRC | GB620806560000 | Lyme Bay East | LYME BAY(C) & RIVER CHAR(S) |  | CHARMOUTH WEST | Commissioned in 2016 - full year data expected in 2022 | 69 | 65 | 65 | 92.4079 | 100% |  |  | Not asset maintenance - Hydraulic capacity | 2022-03-17 | No sewage litter or sewage fungus | 2022-03-17 | TRAC site - N/A |  |  |  | Discharge is 1.2 km out to sea | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620806560000 | No | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=charm&site=ukk2205-21300 |  |  |  | 2025 to 2030 | Installation of 6mm 2D screening | 2005-03-31 | The following Quality improvements are required at this site: 1. Installation of secondary (biological) treatment using an SBR process to treat flows to 3DWF; and 2. Installation of 6mm (2D) prior screening to the settled storm flows to the R. Char. | #N/A | Substandard (WINEP investigation)
13056S | 13056 | 13056S | CHARMOUTH HEADWORKS/SEA OUTFALL WRC - SSO | 401625 | Storm tank at WRC | GB620806560000 | Lyme Bay East | LYME BAY(C) & RIVER CHAR(S) |  | CHARMOUTH WEST | Commissioned in 2016 - full year data expected in 2022 | 4 | 2 | 1 | 0.012778 | 100% | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620806560000 | No | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=charm&site=ukk2205-21300 |  |  |  | 2025 to 2030 |  |  |  | #N/A | Substandard (WINEP investigation)
13060S | 13060 | 13060S | CHIDEOCK MILL LANE WRC - SSO | 401068 | Storm tank at WRC | 267 | Not part of a river WB catchment | RIVER WINNIFORD(S) |  | SEATOWN | Commissioned in 2016 - full year data expected in 2022 | 77 | 62 | 35 | 363.5 | 100% |  |  | Performance - Infiltration | [8 empty] | Not part of a river WB catchment | No | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=seatow&site=ukk2205-21200 |  |  |  | 2025 to 2030 | Provide 6mm screen and 253m3 storage | 2001-12-11 | UV and SO imps | #N/A | Satisfactory but substandard
13250S | 13250 | 13250S | PUNCKNOWLE NEXT TO GULLY KNAP FARM WRC - SSO | 042618 | Storm tank at WRC | GB108044009550 | Bride | RIVER BRIDE |  |  | Commissioned in 2019 - full year data expected in 2022 | 13 | 35 | 46 | 866.5 | 89.62% | Comms failure / issue | Resolved - Jul | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009550 | No |  |  |  |  | 2025 to 2030 |  |  |  | #N/A | Satisfactory
13273B | 13273 | 13273B | SHIPTON GORGE OFF MARKETS LANE SPS | NPSWQD008206 | Storm discharge at pumping station | GB108044009550 | Bride | TRIBUTARY OF THE RIVER BRIDE |  |  | EDM to be installed by December 2023 | [16 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009550 | No |  |  |  |  | tbc |  |  |  | #N/A | #N/A
13334B | 13334 | 13334B | BRIDPORT WEST BAY SPS | 400678 | Storm discharge at pumping station | GB620806560000 | Lyme Bay East | LYME BAY (C) |  |  | Commissioned in 2020 - full year data expected in 2022 | 5 | 9 | 9 | 15.5 | 100% |  |  |  | 2022-03-17 | No sewage litter or sewage fungus | 2022-03-17 | TRAC site - N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620806560000 | No |  |  |  |  | tbc |  |  |  | #N/A | Substandard (WINEP investigation)
13381B | 13381 | 13381B | WEST MILTON WRC - SO/EO | 041658 | Inlet Storm Overflow at WRC | GB108044009590 | Mangerton Brook | TRIB OF MANGERTON RIVER |  |  | Commissioned in 2018 - full year data expected in 2022 | 16 | 5 | 7 | 10.3 | 100% | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009590 | No |  |  |  |  | tbc |  |  |  | #N/A | Satisfactory but substandard (PC)
14404B | 14404 | 14404B | BEAMINSTER SOUTHGATE SPS - SO/EO | 401557 | Storm discharge at pumping station | GB108044009600 | Brit (Upper) | RIVER BRIT |  |  | Commissioned in 2017 - full year data expected in 2022 | 72 | 56 | 43 | 421.7497 | 99.99% |  |  | Not asset maintenance - Hydraulic capacity | 2020-05-01 | Sewage litter present, no sewage fungus | 2020-05-01 | Lab assessment - Impact | 2022-03-01 | Water Quality Modelling shows that the WFD Status Class at the 99%ile level for BOD and Ammonia is High ‘with’ or ‘without’ all Bath FSOs |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009600 | No |  |  |  |  | tbc |  |  |  | #N/A | Satisfactory but substandard
14410B | 14410 | 14410B | BURTON BRADSTOCK BURTON SOUTHOVER SPS - SO/EO | 401968 | Storm discharge at pumping station | GB108044009550 | Bride | RIVER BRIDE (S) |  | HIVE (BURTON BRADSTOCK) | Commissioned in 2016 - full year data expected in 2022 | 2 | 2 | 0 | 0 | 99.95% | [7 empty] | 2021-10-14 | Inaccessible at time of visit |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009550 | No | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=hive&site=ukk2205-20970 |  |  |  | tbc |  |  |  | #N/A | Satisfactory
14413B | 14413 | 14413B | CHIDEOCK SEATOWN SPS - SO/EO | 043190 | Storm discharge at pumping station | 267 | Not part of a river WB catchment | WINNIFORD (S) |  | SEATOWN | Commissioned in 2016 - full year data expected in 2022 | 14 | 6 | 4 | 9.25 | 99.72% | [7 empty] | 2021-10-14 | Baseline data, SO not discharging when sampled |  |  | Not part of a river WB catchment | No | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=seatow&site=ukk2205-21200 |  |  |  | tbc |  |  |  | #N/A | Unsatisfactory
14415B | 14415 | 14415B | LITTON CHENEY CHICKSBRIDGE SPS - SO/EO | 401592 | Storm discharge at pumping station | GB108044009550 | Bride | RIVER BRIDE(S) |  |  | Commissioned in 2019 - full year data expected in 2022 | 170 | 113 | 89 | 1614.9853 | 99.67% |  |  | Performance - Infiltration | 2022-10-28 | No sewage litter or sewage fungus | 2022-10-28 | TBC | 2021-10-14 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009550 | No |  |  |  |  | tbc |  |  |  | #N/A | Substandard (seasonal infiltration)
15481B | 15481 | 15481B | BRADPOLE LEE LANE SPS - SO/EO | 402029 | Storm discharge at pumping station | GB108044009580 | Asker | RIVER ASKER |  |  | Commissioned in 2018 - full year data expected in 2022 | 13 | 9 | 13 | 43 | 99.97% | [7 empty] | 2021-11-17 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009580 | No |  |  |  |  | tbc |  |  |  | #N/A | Satisfactory
15486B | 15486 | 15486B | WEST BEXINGTON SPS - SO/EO | 041125 | Storm discharge at pumping station | GB620806560000 | Lyme Bay East | CHESIL BEACH |  |  | Commissioned in 2017 - full year data expected in 2022 | 66 | 87 | 46 | 302.7664 | 86.74% | Comms failure / issue | Resolved - Oct | Not asset maintenance - Hydraulic capacity | 2018-02-27 | No sewage litter or sewage fungus | 2021-03-10 | Inaccessible | 2021-11-17 | Baseline data, SO not discharging when sampled |  | Outfall in reedbed - cannot always be accessed | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620806560000 | No |  | C00441 | 2023-06-01 | The pumping rate at West Bexington sewage pumping station to Gorselands sewage pumping station will be increased. Both pumping stations will have upgraded pumps and pumping mains. The investment will reduce discharges from 79/year to <20/year. | 2020 to 2025 |  |  |  | #N/A | Substandard (potential WINEP improvement)
15495B | 15495 | 15495B | NETHERBURY BEAMINSTER SPS - SO/EO | 402106 | Storm discharge at pumping station | GB108044009600 | Brit (Upper) | RIVER BRIT |  |  | Commissioned in 2020 - full year data expected in 2022 |  | 33 | 39 | 368.8831 | 99.9% | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009600 | No |  |  |  |  | tbc |  |  |  | #N/A | Satisfactory
15500B | 15500 | 15500B | BRADPOLE FISHWEIR FOUL SPS - SO/EO | 402030 | Storm discharge at pumping station | GB108044009580 | Asker | RIVER ASKER VIA SWS |  |  | Commissioned in 2018 - full year data expected in 2022 | 2 | 0 | 0 | 0 | 100% | [7 empty] | 2021-11-17 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009580 | No |  |  |  |  | tbc |  |  |  | #N/A | Satisfactory
15505B | 15505 | 15505B | SYMONDSBURY WEST ROAD FOUNDRY SPS - SO/EO | 402031 | Storm discharge at pumping station | GB108044010110 | Simene | RIVER SIMENE |  |  | Commissioned in 2018 - full year data expected in 2022 | 40 | 36 | 35 | 210.3331 | 100% |  |  | N/A - Ongoing investigation | 2022-10-28 | No sewage litter or sewage fungus | 2022-10-28 | TBC | 2021-10-14 | Baseline data, SO not discharging when sampled |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044010110 | No |  |  |  |  | tbc | Rebuild, install 6mm raked screen, provide storage 25m3 upsized sewer & telemetry | 2004-03-24 | 1. Install 6mm screening and improve/install telemetry at 3 sites 2. Provide upsized sewer at Chicksbridge SPS to give total storm storage of 25m3 3. Provide a pumped overflow at Broadmayne 4. Rebuild 2 of the overflows (Litton Cheney & Broadmayne) | #N/A | Satisfactory
15507B | 15507 | 15507B | BRIDPORT WEST BAY SLUICES SPS - SO/EO | 402047 | Storm discharge at pumping station | GB620806560000 | Lyme Bay East | BRIDPORT HARBOUR(WEST BAY)(C) |  | WEST BAY (WEST) | Commissioned in 2016 - full year data expected in 2022 | 14 | 13 | 23 | 148.48 | 100% | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620806560000 | No | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=west%20bay&site=ukk2205-21000 |  |  |  | 2025 to 2030 |  |  |  | #N/A | Satisfactory
15651C | 15651 | 15651C | BRIDPORT SOUTH BRIDGE TANK CSO | 400444 | Storm discharge at pumping station | GB108044009580 | Asker | RIVER ASKER(S) |  |  | Commissioned in 2016 - full year data expected in 2022 | 33 | 35 | 26 | 117.6664 | 95.32% | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009580 | No |  |  |  |  | tbc |  |  |  | #N/A | Satisfactory but substandard
15674E | 15674 | 15674E | EYPE PUMPING STATION | 041948 | Emergency Overflow | 267 | Not part of a river WB catchment | RIVER EYPE | N/a | EYPEMOUTH | Commissioned pre-2016 - full year data expected |  |  | 1 | 1.1931 | 100% | [12 empty] | No |  |  |  |  | #N/A |  |  |  | 1 | #N/A
15699E | 15699 | 15699E | NEWLANDS BRIDGE PUMPING STATION | 042371 | Emergency Overflow | GB108044009790 | Char | RIVER CHAR | N/a | CHARMOUTH WEST | Commissioned pre-2016 - full year data expected |  |  | 13 | 65.9311 | 99.98% | [12 empty] | No |  |  |  | Fine screen overflow and separate out surface water flows from caravan park | #N/A |  |  |  | 4 | #N/A
16811C | 16811 | 16811C | BRIDPORT EAST BRIDGE CSO | 402081 | Storm Overflow on sewer network | GB108044009580 | Asker | RIVER ASKER(S) |  |  | Commissioned in 2020 - full year data expected in 2022 |  | 3 | 3 | 2.1 | 100% | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009580 | No |  |  |  |  | tbc |  |  |  | #N/A | Satisfactory
16813C | 16813 | 16813C | BRIDPORT SOUTH STREET DEPOT CSO | 402084 | Storm Overflow on sewer network | GB108044009600 | Brit (Upper) | RIVER BRIT |  |  | Commissioned in 2018 - full year data expected in 2022 | 74 | 59 | 56 | 199.4 | 96.2% |  |  | Not asset maintenance - Hydraulic capacity | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009600 | No |  |  |  |  | tbc | Provision of additional storm tank, 180m3 | 2001-12-11 | Provision of additional storm tank, 180m3 | #N/A | Satisfactory but substandard
16815C | 16815 | 16815C | BEAMINSTER HAMS PLOT SOUTH GATE CSO | 401558 | Storm Overflow on sewer network | GB108044009600 | Brit (Upper) | RIVER BRIT(S) |  |  | Commissioned in 2020 - full year data expected in 2022 |  | 16 | 7 | 11.5 | 100% | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009600 | No |  |  |  |  | tbc |  |  |  | #N/A | Satisfactory
16817C | 16817 | 16817C | BURTON BRADSTOCK GROVE ROAD CSO | 401868 | Storm Overflow on sewer network | GB108044009550 | Bride | RIVER BRIDE(S) |  |  | Commissioned in 2018 - full year data expected in 2022 | 4 | 6 | 4 | 4.7 | 100% | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009550 | No |  |  |  |  | tbc |  |  |  | #N/A | Satisfactory but substandard
16819C | 16819 | 16819C | CHARMOUTH THE STREET ADJ BENHARH CSO | 401594 | Storm Overflow on sewer network | GB108044009770 | Monkton Wyld Stream | RIVER CHAR(S) |  | CHARMOUTH WEST | Commissioned in 2016 - full year data expected in 2022 | 5 | 3 | 0 | 0 | 99.99% | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009770 | No | https://environment.data.gov.uk/bwq/profiles/profile.html?_search=charm&site=ukk2205-21300 |  |  |  | tbc |  |  |  | #N/A | Satisfactory
16821C | 16821 | 16821C | BRIDPORT WEST BRIDGE CSO | 402082 | Storm Overflow on sewer network | GB108044009600 | Brit (Upper) | RIVER BRIT |  |  | Commissioned in 2017 - full year data expected in 2022 | 13 | 18 | 5 | 4.4 | 72.61% | Sensor failure / issue | Resolved - Nov | [9 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009600 | No |  |  |  |  | tbc |  |  |  | #N/A | Satisfactory
16822C | 16822 | 16822C | BRIDPORT WEST STREET CSO | 402083 | Storm Overflow on sewer network | GB108044009600 | Brit (Upper) | RIVER BRIT |  |  | Commissioned in 2017 - full year data expected in 2022 | 59 | 47 | 41 | 64.3333 | 87.64% | Comms failure / issue | Resolved - Sep | N/A - Ongoing investigation | 2020-11-10 | No sewage litter or sewage fungus |  | N/A |  |  |  |  | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009600 | No |  |  |  |  | tbc |  |  |  | #N/A | Satisfactory but substandard
17396C | 17396 | 17396C | BRIDPORT WEST BAY ROAD REAR GARDEN OF 13A CSO | 041198 | Storm Overflow on sewer network | GB108044009540 | Brit (Lower) | RIVER BRIT |  |  | Commissioned in 2020 - full year data expected in 2022 | 0 | 0 | 1 | 0.17 | 100% | [11 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB108044009540 | No |  |  |  |  | tbc | Install 6mm static screen and telemetry | 2004-03-24 | 1. Install 6mm screening and improve/install telemetry at 3 sites 2. Provide upsized sewer at Chicksbridge SPS to give total storm storage of 25m3 3. Provide a pumped overflow at Broadmayne 4. Rebuild 2 of the overflows (Litton Cheney & Broadmayne) | #N/A | Satisfactory but substandard
19539S | 19539 | 19539S | BRIDPORT WYCH FARM WRC | 400673 | Storm tank at WRC | GB620806560000 | Lyme Bay East | LYME BAY(C) |  |  | Commissioned in 2020 - full year data expected in 2022 | 58 | 52 | 40 | 239.54 | 100% |  |  | N/A - Ongoing investigation | [8 empty] | https://environment.data.gov.uk/catchment-planning/WaterBody/GB620806560000 | No |  |  |  |  | 2025 to 2030 | Install 200m3 storage, 4mm powered raked bar screen & replacement pumps | 2005-03-01 | 1. 200 m3 storm storage / settlement tank to serve pumped storm overflow 2. 4mm powered raked bar screen on storm overflow 3. Replacement pass forward pump to achieve at least 31 l/s 4. Replacement 80 l/s duty storm pump and addition of standby storm p | #N/A | Unsatisfactory (WRC FFT)
[40 empty] | Infiltration or PFF/FFT issues | No screen in permit | >20 spills avg over 3 yrs | Old permit | SOAF investigation site | Inv_SOAF_ Infilt | IMP3,5,6 etc | FSO | Satisfactory
[39 empty] | Satisfactory | [8 empty] | x
[39 empty] | Satisfactory but substandard |  | x | x | x | x | x
[39 empty] | Satisfactory but substandard (PC) |  |  |  | x
[39 empty] | Substandard |  | x
[39 empty] | Substandard (potential WINEP improvement) | [7 empty] | x
[39 empty] | Substandard (seasonal infiltration) | x
[39 empty] | Substandard (WINEP investigation) | [7 empty] | x
[39 empty] | Unsatisfactory (SPS PFF) | x
[39 empty] | Unsatisfactory (WINEP) | [6 empty] | x
[39 empty] | Unsatisfactory (WRC FFT) | x
Infiltration or PFF/FFT issues identified on best information currently available - it may prove that the data does not accurately reflect the true problem, if indeed there is a problem
If permit does not include a screening clause, we assume no screen is on site and it is therefore substandard - follow up work here is to check actual asset record to fine tune the data
EDM returns used to generate this data
Only around 50 of our 1300 SOs have not had a permit review in the last 20 years - it is unknown whether or not they are compliant and we have been conservative here, and logged them as substandard until better info is collected
SOAF investigation site in WINEP
SOAF investigation site in WINEP but thought to be affected by infiltration
WINEP imps planned to storm storage, PFF or FFT
WINEP Frequent spilling overflow investigation or improvement
Any remaining sites are assumed to be satisfactory
For 14413 Chideock Seatown SPS, we are currently compliant. To achieve this, we carried out pump testing with the Mechanical Optimisation Team, trialled some different pumps/impellers (as recommended by the MOT) and changed the AV on the rising main. We then installed permanent pumps following the trial.
There are no issues now with FFT at Bridport. Issue was worn impellors on the DWF pumps and a control problem.

## 2022 BS Return SOs
Site ID | Site Name (EA Consents Database) | EA Permit Reference (EA Consents Database) | WaSC Supplementary Permit Ref. [optional] | Storm Discharge Asset Type | WFD Waterbody ID (Cycle 2) (discharge outlet) | WFD Waterbody Catchment Name (Cycle 2) (discharge outlet) | Receiving Water / Environment (common name) (EA Consents Database) | Bathing Water (only populate for storm overflow with a Bathing Water EDM requirement) | Initial EDM Commission Date | Counted spills using 12-24h count method | Total Duration (hrs) all spills prior to processing through 12-24h count method | EDM Operation - % of reporting period EDM operational | Previous Improvements - Most recent AMP period asset previously improved (under BW WINEP driver) | Target Standard affecting Spill Frequency (if SO previously improved) | Spill Frequency for Design Solution (significant spills) (if SO previously improved) | Reason for N/A in previous column
13056 | CHARMOUTH SEWAGE DISPOSAL WORKS | 401625 | 13056C | Inlet SO at WwTW | GB620806560000 | Lyme Bay East | LYME BAY(C) & RIVER CHAR(S) | CHARMOUTH WEST | Commissioned pre-2016 - full BW season data expected | 13 | 4.5225 | 100% | AMP3 (Apr 2000 to Mar 2005) | N/A | N/A | Install 6mm screening
13056 | CHARMOUTH SEWAGE DISPOSAL WORKS | 401625 | 13056S | Storm tank at WwTW | GB620806560000 | Lyme Bay East | LYME BAY(C) & RIVER CHAR(S) | CHARMOUTH WEST | Commissioned pre-2016 - full BW season data expected | 0 | 0 | 100% | AMP3 (Apr 2000 to Mar 2005) | N/A | N/A | Install 6mm screening
13060 | CHIDEOCK STW | 401068 | 13060S | Storm tank at WwTW | 267 | N/A | RIVER WINNIFORD(S) | SEATOWN | Commissioned pre-2016 - full BW season data expected | 1 | 3.5956 | 100% | AMP3 (Apr 2000 to Mar 2005) | Spill Frequency Emission Standard | 3
14410 | BURTON SOUTHOVER PS | 401968 | 14410B | Storm discharge at pumping station | GB108044009550 | Bride | RIVER BRIDE (S) | HIVE (BURTON BRADSTOCK) | Commissioned pre-2016 - full BW season data expected | 1 | 1.5 | 100% | N/A | N/A | N/A
14413 | SEATOWN PUMPING STATION | 43190 | 14413B | Storm discharge at pumping station | 267 | N/A | WINNIFORD (S) | SEATOWN | Commissioned pre-2016 - full BW season data expected | 1 | 0.33694 | 100% | N/A | N/A | N/A
15507 | WEST BAY SLUICES | 402047 | 15507B | Storm discharge at pumping station | GB620806560000 | Lyme Bay East | BRIDPORT HARBOUR(WEST BAY)(C) | WEST BAY (WEST) | Commissioned pre-2016 - full BW season data expected | 3 | 7.3556 | 100% | N/A | N/A | N/A
16819 | THE STREET CSO, CHARMOUTH | 401594 | 16819C | SO on sewer network | GB108044009770 | Monkton Wyld Stream | RIVER CHAR(S) | CHARMOUTH WEST | Commissioned pre-2016 - full BW season data expected | 0 | 0 | 100% | AMP3 (Apr 2000 to Mar 2005) | N/A | N/A | Install 6mm static screen and telemetry
15674 | EYPE PUMPING STATION | 041948 | 15674E | Emergency | 267 | N/A | RIVER EYPE | EYPEMOUTH | Commissioned pre-2016 - full BW season data expected | 1 | 1.1931 | 100%
15699 | NEWLANDS BRIDGE PUMPING STATION | 042371 | 15699E | Emergency | GB108044009790 | Char | RIVER CHAR | CHARMOUTH WEST | Commissioned pre-2016 - full BW season data expected | 0 | 0 | 100%